SYNTHETIC – DEMO ONLY. Fictional company, products and people.

NorthBridge CDMO, site NB-1 — Cleaning and Disinfection of Isolator ISO-2

| Document number | SOP-ENG-080 |
| --- | --- |
| Version | 2.0 |
| Effective date | 15 March 2026 |
| Owner | Head of Engineering |

# 1. Purpose

To define the cleaning and disinfection of Grade A isolator ISO-2 on fill line FL-2.

# 2. Scope

Isolator ISO-2, its gloves and transfer ports. Applies to all products filled on FL-2.

# 3. Responsibilities

Production operators perform the cleaning. QA reviews the cleaning records with the batch record.

# 4. Materials

| Agent | Use |
| --- | --- |
| 70 % isopropyl alcohol (sterile) | Routine wipe after each filling session |
| Sporicide DS-14 (hydrogen peroxide / peracetic acid) | Weekly sporicidal disinfection |
| Vaporised hydrogen peroxide (VHP) | Bio-decontamination cycle |

# 5. Procedure

## 5.1 Routine cleaning after each filling session

Remove all materials from the isolator. Wipe all internal surfaces, gloves and the filling needle holder with sterile 70 % isopropyl alcohol, working from clean to less clean areas.

## 5.2 Weekly sporicidal disinfection

Once per week, and after any Grade A environmental monitoring excursion, apply sporicide DS-14 to all internal surfaces. The surfaces must remain wet for a contact time of at least 10 minutes. Then remove residues with sterile water for injection, followed by 70 % isopropyl alcohol.

## 5.3 VHP bio-decontamination cycle

Run the validated VHP cycle VHP-ISO2-03 before each filling campaign and after any loss of isolator integrity. Release the isolator for use only after the chemical indicators show a pass.

# 6. Records

Record each cleaning in the ISO-2 equipment logbook. Records are retained per SOP-QA-030.